## Slide 1
BOILER SELECTION
Executive
Decision Brief
Pet Factory Maroc · 5 T/H Dry Pet Food Production Line
Fuel:
LPG (Natural Gas — future)
Demand:
2,123 Kg/H (Line 1) · Vision: ×2 in 12 months
Export:
EU + USA · FSSC 22000 · FDA PCAF
PET FACTORY MAROC

## Slide 2
EXECUTIVE SUMMARY
The five decisions that define your boiler strategy
01
Size to Process + Headroom
The contractual 2,123 Kg/H is your process demand. The correct nameplate spec is 2,400–2,600 Kg/H per line — accounting for blowdown losses, LPG efficiency, and startup purging.
02
Two Dedicated Boilers — Not One Shared
One shared oversized boiler is a single point of failure for both lines. Two dedicated units give full operational independence: Line 2 can start, stop, and be maintained without affecting Line 1.
03
Recommend Once-Through Steam Generator (OTSG)
LPG fuel cost makes startup efficiency critical. OTSGs reach full steam in 3–5 minutes vs 30–60 for fire-tube. On LPG, this difference is material over a year of operations.
04
CE Marking is the Only Export-Linked Boiler Requirement
EU and FDA do not specify boiler brands. But your boiler MUST be CE marked under PED 2014/68/EU. Food safety compliance is about steam quality documentation — not the nameplate.
05
Three Shortlisted Manufacturers to Tender
Miura (OTSG, Japan/Europe), Clayton Industries (OTSG, Belgium), Cleaver-Brooks (fire-tube, reference). Minimum three competitive quotes required before any purchase decision.
PET FACTORY MAROC · BOILER SELECTION — EXECUTIVE BRIEFING · CONFIDENTIAL

## Slide 3
WHY THE BOILER IS ON THE CRITICAL PATH
No steam = no conditioning = no extrusion = no production
Raw
Material
Grinding
Batching
& Mixing
Pre-
Conditioner
Extruder
Dryer
Coating
Cooling
Packaging
🔥 STEAM
Pre-Conditioner
Steam + water injected into the dry mix before extrusion. Raises temperature to 80–90°C. Pre-gelatinises starch, denatures pathogens (primary kill step — CCP). Steam pressure must be stable — fluctuation directly impacts product quality and food safety validation.
Extruder Barrel Heating
Indirect steam heating for the six barrel temperature zones (80°C → 160°C). Each zone has a PID-controlled steam coil. Consistent steam pressure is essential for expansion ratio, bulk density, and gelatinisation — the three core quality parameters of the kibble.
Dryer & General Utility
Steam used for dryer pre-heat circuit, oil tank trace heating (2×20,000L tanks must stay liquid), CIP cleaning cycles, and general facility heating. Secondary loads but operationally continuous — the boiler rarely reaches true idle during a production shift.
PET FACTORY MAROC · BOILER SELECTION — EXECUTIVE BRIEFING · CONFIDENTIAL

## Slide 4
SIZING METHODOLOGY
From contract figure to correct nameplate specification
2,123
Kg/H
FAMSUN Contract Spec
≥10%
Headroom
Blowdown + Startup
2,500
Kg/H
Recommended Nameplate
×2
Lines
Vision Year 1 → 5,000 Kg/H
Sizing Element | Specification | Engineering Rationale
FAMSUN contractual steam demand | 2,123 Kg/H | Confirmed scope — conditioner, barrel, dryer circuit
Blowdown loss (LPG, hard water Morocco) | + 150–200 Kg/H | ~7–10% blowdown rate typical for LPG operation
Startup purging & transient peaks | + 100–150 Kg/H | Extruder startup draws peak steam before steady state
Recommended nameplate capacity | 2,400–2,600 Kg/H | Safe operating margin — never run a boiler at nameplate limit
Working pressure specification | 5 bar(g) | Sized above 3 bar(g) minimum — pressure drop in distribution
Steam type | Saturated — dry | Dryness fraction ≥0.95 required. Superheated not needed.
Two-Line Vision: Do NOT buy one 5,000 Kg/H shared boiler. Buy TWO independent 2,500 Kg/H units — one per line. This gives operational independence, N+1 redundancy, partial-load efficiency, and isolatable maintenance without stopping production.
PET FACTORY MAROC · BOILER SELECTION — EXECUTIVE BRIEFING · CONFIDENTIAL

## Slide 5
TECHNOLOGY COMPARISON
Once-Through Steam Generator (OTSG) vs Conventional Fire-Tube Shell Boiler
CRITERIA
OTSG — ONCE-THROUGH
FIRE-TUBE SHELL
Time to Full Steam
3–5 minutes
30–60 minutes
Thermal Efficiency (LHV)
90–95%
82–88%
LPG Startup Cost / Day
Low (fast startup)
High (long purge + heat-up)
Load Following Speed
Near-instant
Moderate (stored energy buffer)
Water Inventory
Minimal (thin tube coils)
Large (pressure vessel full)
Physical Footprint
Very compact
Large — 6m+ length typical
Purchase Price
Higher (+20–35%)
Lower baseline
Spare Parts in Morocco
Import required
More local availability
Operating Complexity
Lower — no blowdown vessel
More procedures required
5-Year TCO on LPG
Lower (efficiency savings)
Higher (LPG waste on startup)
VERDICT: OTSG recommended for LPG fuel + food processing + compact footprint. Fire-tube remains valid if spare parts availability is the priority constraint.

## Slide 6
LPG FUEL — SPECIFIC ENGINEERING CONSIDERATIONS
LPG changes the economics and the engineering requirements significantly
🔥 Higher Calorific Value = Higher Flame Temperature
LPG burns hotter than natural gas (approximately 93.2 MJ/m³ vs 38.5 MJ/m³). Every boiler and burner must be FACTORY-RATED for LPG. Never accept a field conversion from natural gas — combustion characteristics, excess air settings, and flame stability require OEM calibration.
💰 LPG Cost Makes Startup Efficiency Critical
LPG in Morocco costs approximately 40–60% more per energy unit than piped natural gas. Every cold startup of a conventional fire-tube boiler burns 60–90 minutes of LPG heating water that is not producing usable steam. On a 5-day/week line with one shutdown per weekend, this is a measurable annual cost difference vs an OTSG.
🏗 Bulk LPG Tank — Separate Civil Scope
A 10–15 tonne bulk LPG tank is required on-site. This is NOT included in boiler quotes. You need a vaporiser (forced if site elevation or cold winters), pressure regulation train, gas detection system, and fire safety bund. Budget this as a separate CAPEX item. Lead time for bulk tank delivery to Morocco: 8–14 weeks.
🌡 Vapour Pressure and Ambient Temperature
LPG loses vapour pressure at low ambient temperatures. For most Moroccan coastal and lowland sites this is rarely a problem, but if your site is inland or above 400m elevation, specify a forced electric vaporiser in your LPG installation scope. Your LPG supplier must confirm the design ambient and tank sizing.
⚙ Burner Commissioning and Combustion Analysis
LPG burner commissioning requires a flue gas analyser (O₂, CO, CO₂) to set the correct excess air ratio. This must be done by a certified LPG combustion engineer, not a general boiler technician. Request this as part of your commissioning scope in the tender documents.
📋 Future Gas Upgrade — Specify Dual-Fuel Burner Now
If natural gas becomes available at your site in 3–5 years (ONEE gas grid expansion is ongoing in Morocco), a dual-fuel LPG/natural gas burner installed today avoids a complete burner replacement later. The incremental cost at purchase is modest. Recommend specifying dual-fuel as an option in your tender.
PET FACTORY MAROC · BOILER SELECTION — EXECUTIVE BRIEFING · CONFIDENTIAL

## Slide 7
EU & USA EXPORT — WHAT ACTUALLY MATTERS
The boiler brand does not determine your export certification. These five things do.
Key Principle: No EU regulation or FDA rule specifies a boiler brand or technology type. What is regulated is the safety and traceability of what the boiler produces — steam as a food contact input — and how you document it.
01
CE Marking under PED 2014/68/EU
This is the ONE area where your boiler selection directly affects export readiness. A boiler sold into Morocco may carry only Moroccan certification. For EU market credibility and FSSC 22000 audit defensibility, insist on CE marking in your tender. European-sourced Miura, Clayton, or Cleaver-Brooks units come CE marked as standard.
🇪🇺 EU
02
Food-Grade Boiler Water Treatment (NSF H1)
Standard industrial anti-scale and oxygen-scavenging chemicals are NOT acceptable when steam contacts food. Both EU Reg. 183/2005 and FDA 21 CFR Part 507 require chemical inputs to be food-grade. Specify NSF H1 certified water treatment chemicals in your tender as a mandatory requirement. Your chemical supplier must provide a certificate.
🇪🇺 EU
🇺🇸 USA
03
Steam Quality as a Documented CCP
Your HACCP plan must identify the conditioner steam circuit as a Critical Control Point. You need a monitoring SOP (daily pH, conductivity, chemical residue), corrective action procedure, and independent laboratory steam quality test results (quarterly). An auditor will ask for these records — the boiler brand is irrelevant, the records are everything.
🇪🇺 EU
🇺🇸 USA
04
Calibration Traceability on All Instruments
Every pressure gauge, temperature sensor, safety valve, and conductivity meter on the boiler must be calibrated by an accredited body, with certificates retained for minimum 2 years. Both FSSC 22000 and FDA PCAF auditors will sample these records. Build calibration into your commissioning scope — do not treat it as an afterthought.
🇪🇺 EU
🇺🇸 USA
05
Consistent Steam Supply to the Kill Step
The conditioner + extrusion kill step (≥80°C, ≥30 seconds) is your primary food safety barrier. Your HACCP validation must demonstrate the boiler can maintain this consistently throughout a production run. OTSG's superior load-following makes this validation evidence cleaner — but any boiler that can hold pressure under variable demand is acceptable if documented.
🇪🇺 EU
🇺🇸 USA
PET FACTORY MAROC · BOILER SELECTION — EXECUTIVE BRIEFING · CONFIDENTIAL

## Slide 8
MANUFACTURER LANDSCAPE
Shortlisted vendors — based on confirmed knowledge, no speculation
⚠ Transparency Note: Manufacturer knowledge is based on verifiable industry information. Pricing, current Morocco availability, and lead times must be confirmed directly with each vendor before any commitment.
PRIMARY
MIURA
Japan / Europe · OTSG
Model: LX / EX series — compact, fast-startup
Food Industry
Pharmaceutical & food industry standard globally
CE Marked
Yes — European-sourced units
LPG
LPG-rated burners available
Service Africa
European office (UK, France) — verify North Africa distributor
Reference name for OTSG in food processing. Fast startup and high efficiency most relevant to your LPG context.
PRIMARY
CLAYTON INDUSTRIES
USA / Belgium · OTSG
Model: Series E / EG — vertical coil OTSG
Food Industry
Food & beverage, industrial process
CE Marked
Yes — manufactured in Belgium
LPG
LPG configurations available
Service Africa
Belgium manufacturing — strong EU logistics to Morocco
Belgian manufacturing base is a logistics advantage for Morocco vs Japan. Include in tender alongside Miura.
ALTERNATIVE
CLEAVER-BROOKS
USA / Global · Fire-Tube
Model: CBex / ClearFire series
Food Industry
Broad industrial including food
CE Marked
CE models available on European range
LPG
LPG burners standard option
Service Africa
Broad global network — verify North Africa
If fire-tube is preferred for spare parts availability, Cleaver-Brooks is the international reference. Proven reliability but lower efficiency on LPG.
ALTERNATIVE
FULTON
USA / UK · OTSG / Fire-Tube
Model: VSRT series (spiral rib tube — hybrid)
Food Industry
Food & beverage sector track record
CE Marked
Yes — UK manufactured
LPG
LPG available
Service Africa
UK distribution — verify North Africa agent
Interesting hybrid technology between OTSG and fire-tube. Good food industry track record in Europe.
REGIONAL
ICI CALDAIE
Italy · Fire-Tube
Model: ICI TIGON / ELIA series
Food Industry
Industrial process including food
CE Marked
Yes — Italian manufactured
LPG
LPG configurations available
Service Africa
Strong Mediterranean & North Africa distribution network
Geographic proximity advantage — Italian suppliers have historically strong distribution in Morocco and North Africa. Spare parts access likely better than Japanese or US brands.
PET FACTORY MAROC · BOILER SELECTION — EXECUTIVE BRIEFING · CONFIDENTIAL

## Slide 9
TOTAL COST OF OWNERSHIP — 5-YEAR ANALYSIS
LPG economics fundamentally change the CAPEX vs OPEX trade-off
Cost Category | OTSG | Fire-Tube | Key Driver
Purchase Price | Higher +20–35% | Lower — baseline | Fire-tube has lower CAPEX. Difference narrows with commissioning included.
LPG Fuel — Daily Startup Cost | Low (3–5 min startup) | High (30–60 min startup) | ~55 min × daily startup × LPG rate × 300 days/year = significant annual delta
LPG Fuel — Operating Efficiency | 90–95% thermal efficiency | 82–88% thermal efficiency | 7% efficiency gap × LPG cost × 2,500 Kg/H output = large annual saving
Water Treatment Chemicals | Lower (minimal blowdown) | Higher (blowdown losses) | Blowdown wastes treated water and energy — adds to annual OPEX
Maintenance Labour | Lower — fewer procedures | Higher — blowdown, vessel checks | OTSG has simpler daily operating procedures
Spare Parts (Morocco context) | Higher — import required | More locally available | Fire-tube has advantage on parts availability in Morocco
Annual Inspection (regulatory) | Required both | Required both | Moroccan pressure vessel law applies to both technologies equally
5-Year TCO on LPG | LOWER overall | HIGHER overall | OTSG efficiency premium pays back in 2.5–3.5 years on LPG
LPG Payback Logic: At 7% higher thermal efficiency and 55 minutes less startup time per day, the OTSG OPEX saving on LPG pays back the CAPEX premium in approximately 2.5–3.5 years depending on LPG market price and annual operating hours. This analysis should be run with your LPG supplier's confirmed unit price before final vendor selection.
PET FACTORY MAROC · BOILER SELECTION — EXECUTIVE BRIEFING · CONFIDENTIAL

## Slide 10
RECOMMENDED CONFIGURATION
Engineering recommendation for Pet Factory Maroc
✅ TWO INDEPENDENT OTSG UNITS — One Dedicated per Production Line
Miura LX series or Clayton Industries Series E · 2,400–2,600 Kg/H each · 5 bar(g) · LPG with dual-fuel option · CE marked
BOILER 1
OTSG 2,500 Kg/H
BOILER 2
OTSG 2,500 Kg/H
PRODUCTION
LINE 1 — 5 T/H
PRODUCTION
LINE 2 — 5 T/H
(Year 1 Vision)
STEAM →
STEAM →
Operational Independence
Each line starts, stops, and is maintained independently. Line 1 production is never affected by Line 2 boiler maintenance.
N+1 Redundancy Built-In
If Boiler 1 trips, Line 1 slows but does not stop if Boiler 2 can cross-supply temporarily via a header cross-connection valve.
Partial Load Efficiency
When only Line 1 operates, Boiler 2 is offline. Each boiler runs at its design point — no efficiency penalty from part-loading a large shared vessel.
HACCP Simplification
Each boiler serves one production line — traceability is direct. If a steam quality issue occurs, affected product is limited to one line.
LPG Infrastructure: One shared 15T bulk LPG tank + vaporiser serves both boilers. Specify dual-fuel burners (LPG + future NG) to protect against future fuel switch.
PET FACTORY MAROC · BOILER SELECTION — EXECUTIVE BRIEFING · CONFIDENTIAL

## Slide 11
RISK REGISTER
Key risks and mitigations for boiler selection and commissioning
Risk | Impact | Prob. | Mitigation & Owner
LPG supply disruption — no backup fuel | HIGH | MED | Specify dual-fuel burner (LPG + NG) at purchase. Maintain minimum 10T LPG buffer stock on-site at all times. Define emergency procedures.
Boiler delivery delay — China/Europe lead times | HIGH | MED | Boiler is on the critical path. Issue PO as first equipment order. For European OTSGs (Clayton Belgium, Miura UK): 12–20 weeks typical. Track weekly.
OTSG spare parts not available in Morocco | MED | HIGH | Negotiate a 2-year critical spare parts package in the purchase contract. Stock locally: coils, burner nozzles, sensors, safety valve, BMS controller.
Single LPG supplier — price or supply risk | MED | MED | Contract with two LPG suppliers before commissioning. Negotiate a fixed-price contract for Year 1 to protect against LPG price volatility.
Steam quality out of spec — HACCP failure | HIGH | LOW | NSF H1 chemicals from day one. Daily water quality log. Quarterly independent steam lab test. CCP monitoring SOP in place before first export.
Pressure vessel cert not obtained pre-commissioning | HIGH | LOW | Engage Moroccan certified inspection authority immediately. Annual cert is a legal operating requirement — no cert = cannot run the boiler legally.
LPG burner field-converted from natural gas | HIGH | LOW | Specify in tender: LPG burner must be factory-rated and calibrated — no field conversions accepted. Include this as a mandatory contract requirement.
Boiler oversized for actual steam demand | MED | MED | Obtain FAMSUN steam consumption table per process step before issuing boiler PO. Validate 2,123 Kg/H figure is confirmed and complete.
PET FACTORY MAROC · BOILER SELECTION — EXECUTIVE BRIEFING · CONFIDENTIAL

## Slide 12
TENDER SPECIFICATION
Mandatory requirements to include in every boiler enquiry document
MANDATORY TECHNICAL SPECS
◆ Nameplate output: 2,400–2,600 Kg/H minimum
◆ Working pressure: 5 bar(g) design
◆ Steam type: Saturated, dryness fraction ≥0.95
◆ Fuel: LPG primary, dual-fuel (LPG + NG) preferred
◆ Thermal efficiency: ≥90% LHV on LPG
◆ CE marked under PED 2014/68/EU — mandatory
◆ MAWP and design code stamped on pressure vessel
◆ Safety relief valve: factory-set, sized to pass full output
◆ Low water level cutout: independently tested
◆ Automatic flue gas purge: 4× furnace volume before ignition
MANDATORY FOOD SAFETY SPECS
◆ NSF H1 certified water treatment chemicals — supplier cert required
◆ No copper or zinc alloy fittings in steam circuit
◆ Steam sampling point with isolation valve
◆ Condensate quality monitoring provision
◆ All instruments calibration-ready with certificate provision
◆ BMS with data logging output (4–20mA or Modbus TCP)
◆ Daily operating log template included in commissioning docs
◆ HACCP documentation support from supplier on request
SCOPE OF SUPPLY — MANDATORY
◆ Complete water treatment package (softener + deaerator + dosing)
◆ Bulk LPG storage scope or interface documentation
◆ Full commissioning by OEM engineer — not subcontracted
◆ LPG combustion analysis at commissioning — certified engineer
◆ Operator training: minimum 2 days, in English or French
◆ Spare parts package: 2-year critical inventory quoted
◆ O&M manual in English or French — mandatory
◆ CE Declaration of Conformity issued at delivery
◆ Pressure vessel test certificate at factory + site
PET FACTORY MAROC · BOILER SELECTION — EXECUTIVE BRIEFING · CONFIDENTIAL

## Slide 13
IMPLEMENTATION ROADMAP
From decision to first steam — critical path milestones
01
Validate Steam
Demand
NOW — 2 Weeks
◆ Obtain FAMSUN steam consumption table per process step
◆ Verify 2,123 Kg/H is confirmed total — not estimate
◆ Confirm FAMSUN conditioner inlet pressure requirement
◆ Confirm steam demand for dryer, CIP, trace heating separately
02
Confirm LPG
Infrastructure
NOW — 2 Weeks
◆ Confirm LPG supplier and delivery logistics to site
◆ Confirm site access for 15T bulk tank installation
◆ Engage civil team for LPG bund and gas detection scope
◆ Decision: dual-fuel burner now or LPG-only?
03
Issue Tender
& Select
Weeks 2–6
◆ Issue RFQ to Miura (EU office), Clayton Industries, Cleaver-Brooks
◆ Mandatory: CE marking, LPG rating, NSF H1 compatibility
◆ Request OTSG and fire-tube alternatives for comparison
◆ Evaluate on 5-year TCO, not purchase price alone
04
Place Order
& Track
Week 6–8
◆ Issue PO — boiler is on critical path to commissioning
◆ Request Factory Acceptance Test (FAT) date at manufacture
◆ Engage Moroccan pressure vessel inspection authority now
◆ Start water treatment package procurement in parallel
05
Install &
Commission
Per Gantt
◆ Boiler room civil works complete before delivery
◆ Commissioning: utilities first — boiler before extruder trials
◆ LPG combustion analysis by certified engineer
◆ Safety valve test, low-water cutout test — documented
06
Food Safety
Validation
Post-Commission
◆ First steam quality sample to accredited laboratory
◆ HACCP plan: conditioner steam documented as CCP
◆ Daily boiler log system operational
◆ Annual pressure vessel inspection scheduled and booked
PET FACTORY MAROC · BOILER SELECTION — EXECUTIVE BRIEFING · CONFIDENTIAL

## Slide 14
KEY DECISIONS REQUIRED FROM EXECUTIVE TEAM
DECIDE NOW
Engineering + Procurement
Confirm LPG as fuel and initiate bulk LPG tank design + supplier contract
Why: Boiler tender cannot be issued without fuel specification confirmed. LPG tank is 8–14 week lead time.
DECIDE NOW
Engineering
Obtain FAMSUN steam consumption table — validate 2,123 Kg/H before ordering
Why: If the actual demand differs from the contract figure, you risk ordering the wrong size boiler.
DECIDE NOW
Executive Team
Approve two-boiler strategy (one per line) vs single shared unit
Why: This is a CAPEX decision. Two units costs more upfront but is strongly recommended for operational resilience and Line 2 independence.
WEEK 1–2
Procurement
Approve OTSG technology direction and issue RFQ to Miura, Clayton, Cleaver-Brooks
Why: Minimum three vendors needed for competitive tender. Boiler is on the commissioning critical path — delay here delays first production.
WEEK 1–2
Engineering
Specify dual-fuel burner (LPG + Natural Gas) as preferred option in tender
Why: Future gas grid connection to site is possible in 3–5 years. Dual-fuel option at purchase avoids a complete burner replacement later.
WEEK 2–4
Engineering + Quality
Engage NSF H1 certified boiler water treatment chemical supplier
Why: Food-grade water treatment is mandatory for EU and USA export. Standard industrial chemicals are not acceptable — replace before commissioning.
WEEK 2–4
Regulatory / Engineering
Identify and engage Moroccan certified pressure vessel inspection authority
Why: Annual inspection certificate is a legal operating requirement. Cannot commission the boiler without this in place.
PET FACTORY MAROC · BOILER SELECTION — EXECUTIVE BRIEFING · CONFIDENTIAL