## Slide 1
BOILER
SYSTEM
Key Factors for Dry Pet Food Production
2,123 Kg/H · Rated Steam Output
PET FACTORY MAROC

## Slide 2
ROLE IN THE PRODUCTION LINE
The boiler is the first utility to commission — no steam means no conditioning, no extrusion, no production.
Raw
Material
Grinding
Batching
& Mixing
Condition
+ Extrude
Drying
Coating
Packaging
◆ STEAM
Conditioner Steam
Injected ahead of the extruder. Raises mix to 80–90°C. Pre-gelatinizes starch, denatures pathogens. Critical for consistent extrudate quality.
Extruder Barrel Heating
Indirect steam for barrel zone temperatures (80→160°C). Controls expansion ratio, bulk density, and starch gelatinization percentage.
Dryer & Utility
Hot water and steam for dryer air circuit, oil tank trace heating, CIP cleaning, and general facility services.
PET FACTORY MAROC · BOILER SYSTEM

## Slide 3
TECHNICAL SPECIFICATIONS
2,123
Kg/H
Steam Output
1–3
bar(g)
Working Pressure
Saturated
Steam Type
No Superheat Needed
Annual
Certification
Pressure Vessel Inspection
Parameter | Value | Notes
Rated steam output | 2,123 Kg/H | For one 5 T/H pet food line
Steam type | Saturated steam | Superheated not needed for conditioning
Working pressure | 1.0 – 3.0 bar(g) | Confirm with FAMSUN conditioner spec sheet
Fuel | Natural gas (preferred) | LPG backup — Morocco gas availability TBC
Feed water quality | Softened + deaerated | Hardness <50 ppm, O₂ <0.02 ppm
Blowdown | Daily manual + weekly auto | Conductivity-controlled auto blowdown preferred
Safety valve | Set at 110% MAWP | Mandatory — sized to pass full boiler output
Annual inspection | Pressure vessel certification | Moroccan regulatory authority — legally mandatory
PET FACTORY MAROC · BOILER SYSTEM

## Slide 4
INSTALLATION REQUIREMENTS
Civil & Structural
Dedicated boiler room — fire-rated walls (2hr min)
Concrete plinth for boiler weight + water load
Secondary containment bund for condensate
Min 1.0m clearance on all sides for maintenance
Roof ventilation / explosion relief panels
Fixed gas detection system (Class 1 Div 2)
Utilities Connections
Natural gas supply line — sized for boiler BTU
Cold water makeup — softened, pressure-regulated
Blowdown drain to neutralization pit
Steam main header to conditioner & barrel zones
Condensate return line (energy recovery)
3-phase electrical — boiler controls & BMS
Water Treatment System
Softener (ion exchange) — mandatory
Deaerator or chemical O₂ scavenging
Conductivity meter on feed water
Chemical dosing: anti-scale, anti-corrosion
Sample points: feed, boiler water, steam
Daily water quality log — regulatory requirement
PET FACTORY MAROC · BOILER SYSTEM

## Slide 5
COMMISSIONING SEQUENCE
01
Pre-Commissioning Checks
Pipework pressure-tested (1.5× MAWP)
Safety valves bench-tested & certified
Feed water system flushed & sampled
Gas leak test on all joints
BMS wiring verified & loop-tested
02
Cold Commissioning
Fill boiler with treated feed water
Check all instrumentation — P, T, level
Verify auto blowdown sequence
Test low-water level cutout (mandatory safety)
Check all interlocks and alarms
03
Warm-Up & Steam Raise
Controlled heat-up rate <55°C/hour
Purge gas line before ignition
Pilot burner test then main burner light-off
Monitor for leaks during pressurization
Raise to working pressure gradually
04
Performance Verification
Confirm 2,123 Kg/H at working pressure
Measure steam dryness fraction >0.95
Record fuel consumption vs. output
Verify condensate return flow & temp
Document all settings — operations baseline
PET FACTORY MAROC · BOILER SYSTEM

## Slide 6
MAINTENANCE & SAFETY
PREVENTIVE MAINTENANCE
DAILY
Blowdown · Feed water chemistry · Burner flame check · Log P & T
WEEKLY
Bottom blowdown · Safety valve check · Gas train inspection · Water sample
MONTHLY
Safety valve pop test · Combustion analysis · Heat exchanger tubes · BMS alarms
QUARTERLY
Internal inspection (cooled) · Clean waterside scale · Refractory lining check
ANNUAL
Pressure vessel inspection — certified authority (mandatory) · Full retubing assessment
⚠ SAFETY CRITICAL ITEMS
Low Water Level Cutout
Must trip burner before tubes are exposed. Test monthly. Failure = tube burnout / explosion risk.
Safety Relief Valve
Sized to pass full output. Must open before MAWP. Cannot be isolated or bypassed under any circumstances.
Automatic Flue Gas Purge
Mandatory 4× furnace volume purge before every ignition. Prevents unburned gas explosion.
Gas Train Standards
Dual-block isolation valves, pressure regulators per EN 746-2. Leak-test on each startup.
Pressure Vessel Certification
Moroccan law requires annual inspection. Operating without cert = illegal and uninsured.
PET FACTORY MAROC · BOILER SYSTEM

## Slide 7
RISK REGISTER
Risk | Impact | Prob. | Mitigation
Natural gas supply not confirmed at site | HIGH | MED | Confirm ONEE gas line availability. Size LPG backup tank as interim solution.
Boiler delivery delay (China lead time ~14 wks) | HIGH | MED | Boiler on critical path — extruder cannot run without steam. Order immediately, track weekly.
Feed water hardness causes scale buildup | MED | HIGH | Install softener + deaerator before commissioning. Daily water quality log is mandatory.
Pressure vessel cert not obtained before run | HIGH | LOW | Engage certified Moroccan inspection authority before FAT. No cert = cannot operate legally.
Boiler oversized for actual steam demand | MED | MED | Verify conditioner + barrel heating loads vs. 2,123 Kg/H spec before final order.
Condensate not recovered — energy waste | LOW | HIGH | Install condensate return system. Recover >80% to cut fuel cost and feed water demand.
PET FACTORY MAROC · BOILER SYSTEM

## Slide 8
KEY DECISIONS & NEXT STEPS
NOW
Engineering
Confirm exact steam demand from FAMSUN conditioner + extruder spec sheets vs. 2,123 Kg/H
NOW
Procurement
Confirm natural gas availability at site — if unavailable, order LPG interim tanks
WEEK 1
Procurement
Issue boiler PO — lead time is on the commissioning critical path
WEEK 2
Civil
Complete boiler room design — fire-rated walls, ventilation, bund, gas detection
WEEK 2
Engineering
Design and order water treatment system (softener + deaerator + chemical dosing)
WEEK 4
Regulatory
Identify Moroccan pressure vessel inspection authority — engage before FAT
WEEK 4
Engineering
Define steam distribution P&ID — header + branch lines to conditioner and barrel zones
PET FACTORY MAROC · BOILER SYSTEM